# Scope of Work

To design, supply and install an Analogue Addressable Fire Alarm Control System in accordance with the details specified herein and in accordance with supplied drawings.

The system shall include all materials, equipment and wiring required to install the complete Fire Detection and Alarm System. The system shall include but not be limited to one or more control panels, repeater panels, and sensors, call points, audible and visual alarm indicating devices and relays.

The installation shall include the installation of all cables required for connection of the detection, alarm indicating and other devices along with connections to the power supply as appropriate to the design. All cabling shall conform to the requirements and recommendations of the Fire Alarm Control Panel manufacturer. Any openings /chasings in walls, ceilings or floors shall be made good.

The system shall be designed such that no more than 90% of the available signalling / detection loop capacity is employed to allow for future requirements.

# Standards

The fire detection system shall be designed, installed and commissioned in accordance with, and all elements shall meet the requirements of BS5839-1: 2013 Code of Practice and EN 54-2:1997+A1:2006.  The responsible company should be able to demonstrate their competence to design, install and commission the system, e.g. by certification to BAFE SP203, LPS1014 or other relevant standard.

The equipment manufacturer shall operate a quality management system in accordance with ISO 9001:2000. In addition, the equipment shall be manufactured under a recognised factory control procedure such as the BSI Kitemark scheme.

All detection devices shall be independently certified as complying with the relevant EN54 standard.

# Intelligent Devices - Basic Requirements

The system should have the ability of utilising sub-addressing with both devices and modules to increase the overall capacity on each loop.

# Addressable Units

The manufacturer shall be capable of offering intelligent versions of the following units, taking only one address from the loop:

Optical smoke sensors

Heat sensors

Multi sensors

Optical beam smoke detectors

Conventional detector interface module

Addressable sounder modules (sub-addressing to all inputs& outputs)

Addressable relay interface modules (sub-addressing to all inputs& outputs)

Addressable switch monitoring modules (sub-addressing to all inputs& outputs)

Short circuit isolator modules (no address required)

Loop powered base and wall sounders (sub-addressing to extend number of addresses in conjunction with a sensor)

Loop powered visual devices such as beacons and remote indicators, including EN54-23 compliant devices

Manual call points for indoor use

Manual call points for outdoor use

Multiple inputs/outputs (sub-addressing to all inputs& outputs)

## Sensors - General

All three sensors types (Optical, Heat and Multi) should be available in these variants:

- With Marine approval

- With SIL Level 2 approval

- With integrated short-circuit isolator

All sensors should also incorporate a locking mechanism, utilised by removing a plastic tab from the underside of the sensor, which once locked onto the base means the sensor can only be removed with a special removal tool.

All sensors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

All sensors shall incorporate two LEDs, clearly visible from the outside, to provide indication of status.  The LEDs should be controlled from the FACP if the LEDs flash during the normal polling sequence.  The LED colour shall indicate status:

| Green - blinking | Polling (communicating with FACP) |
| --- | --- |
| Amber - solid | Active short-circuit isolation (for SCI variants only) |
| Red - solid | Alarm condition |

In locations where the sensor is not readily visible, remote indicator units shall be provided.

## Optical Smoke Sensor – Intelligent Addressable

The optical smoke sensor shall be capable of detecting visible combustion gases emanating from fires and shall employ the forward light-scatter principle.

The optical smoke chamber shall be equally sensitive to a wide range of combustible materials and incorporate flat response technology.  The sensor should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the detector, once locked onto the base the detector can only be removed with a special removal tool.

The design of the point-type optical smoke sensor sensing chamber shall be optimised to minimise the effect of dust deposit over a period of time.  The chamber cover shall be removable for ease of cleaning or replacement.

Polling LEDs located on the optical smoke sensor can be switched off via the FACP.

The point-type optical smoke sensors shall incorporate screens designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).

The optical smoke sensors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

The manufacturer shall have available the following versions of the point type optical smoke sensor to meet different applications:

Intelligent addressable

Marine Approved

Approved to SIL2

The optical smoke sensor shall incorporate two LEDs, clearly visible from the outside, to provide indication of alarm actuation.

In locations where the detector is not readily visible, remote indicator units shall be provided.

## Multi-Sensor – Intelligent Addressable

The multi-sensor offering should consist of a model either capable of monitoring the environment with two different sensing elements or a model with three different sensing elements:

| 2 Sensing Elements | 3 Sensing Elements |
| --- | --- |
| Optical | Optical |
| Thermal | Thermal |
|  | Carbon Monoxide (CO) |

The design of the point-type multi-sensor optical smoke detector sensing chamber shall be optimised to minimise the effect of dust deposit over a period of time.  The chamber cover shall be removable for ease of cleaning or replacement.  The sensor should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the sensor, once locked onto the base the detector can only be removed with a special removal tool.

The point-type multi-sensors shall incorporate screens designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).

The multi-sensors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

The multi-sensor should be able to operate in a minimum of 24 approved operating modes, using various combinations of each sensing element, that can be matched to the installation environment.

The CO sensing cell should have a manufacturer’s guaranteed life span of 10 years.

The sensor should feature software enhancements to reduce false alarms.

The multi-sensor shall incorporate two LEDs, clearly visible from the outside, to provide indication of alarm actuation.  The LEDs should be controlled from the FACP if the LEDs flash during the normal polling sequence.

The modes of the multi-sensor should be controlled by the FACP, when the FACP changes from one mode to another the FACP should re-calibrate the multi-sensor.

In locations where the detector is not readily visible, remote indicator units shall be provided.

The multi-sensor should have the capability of monitoring any of the sensing elements, if either of the elements fail it should be reported and displayed at the FACP.

## Heat Sensor – Intelligent Addressable

The heat sensors shall be capable of detecting rapid rise in temperature and/or fixed absolute temperatures.

The heat sensors shall employ two heat-sensing elements with different thermal characteristics to provide a rate of rise dependent response.

The heat sensors shall include RFI screening to minimise the effect of radiated and conducted electrical interference.  The sensor should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the detector, once locked onto the base the detector can only be removed with a special removal tool.

The manufacturer shall have available the following versions of heat sensors to meet different applications:

Intelligent addressable – Class A, B & C (should be approved to SIL2)

Intelligent addressable – IP rated 67, Class A, B & C

The heat sensor shall incorporate two LEDs, clearly visible from the outside, to provide an indication of alarm actuation.

In locations where the detector is not readily visible, remote indicator units shall be provided.

## Sensor Base

The automatic point-type fire sensors shall be fixed to the installation by means of screw-fit bases.

The base specified shall incorporate the optional feature of being able to lock the sensors in place once plugged in.  Termination facilities shall be available for cable screen termination.

Standard intelligent addressable bases shall not contain any electronic circuitry with exception to the isolator variants.  This shall enable insulation and continuity checks to be completed on the wiring with the detector heads removed.

Standard intelligent addressable bases should be capable of supporting sensors, beacons, remote indicators, VADs, sounders and sounder/VADs without the need to physically change base types.

Standard. isolator variant should be approved to SIL

## Intelligent Addressable Beam Smoke Detector

The intelligent addressable beam smoke detector should be of a reflective motorized type and be able to provide a detection range of between 5 m and 100 m.  The unit should be loop-powered and be capable of continually and automatically correcting its alignment without intervention.  Ideally, the detector head should be commissioned and controlled from ground level utilising a control unit to avoid working at height.

## Intelligent Addressable Manual Call Points

The intelligent addressable manual call points shall monitor and signal to the FACP the status of a switch operated by a “non-frangible element” assembly.  They shall be red in colour and suitable for surface or flush mounting.  The addressable call points shall be provided with an integral red LED to indicate activation.  The polling LED can be switched off from the FACP.  There should be an optional call point cover that can be fitted to prevent accidental operation.

An intelligent addressable weatherproof call point shall be available affording protection to IP 66.

The intelligent addressable call points shall be capable of operating by means of thumb pressure and not require a hammer.  They shall be capable of being tested using a special ‘key’ and feature a non-frangible, resettable element instead of a glass.

The intelligent addressable call points shall incorporate a mechanism to interrupt the normal addressable loop scan to provide an alarm response within 3 seconds and shall be field programmable to trigger either an alert or an evacuate response from the FACP.

The unit should also be available as an integral SCI (short-circuit isolator) variant, both for internal and external use.

The intelligent addressable manual call point should be approved to SIL2.

## Intelligent Addressable Loop Powered Beacon

The intelligent addressable beacon is a visual indicating device that can be fitted onto the isolator base or standard base.

The beacon shall have its address programmed via a hand-held address tool, and the lens should be available in red, blue or amber with a flash rate of 1 Hz.

The beacon should also incorporate a locking mechanism which is utilised by removing a plastic tab from the underside of the beacon.  Once locked onto the base, the beacon can only be removed with a special removal tool as per a sensor.

## Intelligent Addressable Sounder Module

The intelligent addressable sounder module shall be capable of monitoring and controlling two independent circuits of alarm sounders using a single loop address.

24 Vdc power to drive the sounders shall be derived independently or from the FACP.

The addressable sounder module shall be capable of operating both sets of sounders in a pulsing or continuous mode as determined on the module. Each circuit shall be individually programmable. Sounder circuits shall be capable of synchronisation.

The intelligent addressable sounder module shall provide the facility to monitor the wiring to the sounders for open or short-circuit and transmit the necessary fault signal to the FACP. Each sounder circuit shall be separately fused.

The intelligent addressable sounder module shall provide the facility to monitor for failure of the power supply for the sounders and transmit the necessary fault signal to FACP.

The intelligent addressable sounder module shall provide a green LED indication when polled by the FACP.

The intelligent addressable sounder module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable sounder module should only have one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Intelligent Addressable Powered Output Module

The intelligent addressable powered output module shall incorporate two monitored inputs and have a 24 Vdc output with selectable current levels, these should range from 2 mA to 32 mA (in 2 mA increments) the module should use a single loop address, and the current levels should be programmed from the FACP.

The intelligent addressable plant control module should only use one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

The unit should be addressed electronically using a hand-held tool and special lead.

## Intelligent Addressable Single Input Module

The intelligent addressable single input module incorporates one monitored input.

The intelligent addressable plant control module should only use one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

The unit should be addressed electronically using a hand-held tool and special lead.

## Intelligent Addressable Single Output Module

The intelligent addressable single output module incorporates one monitored output – incorporates a volt free relay unit and can be configured N/O or N/C rated to 30Vdc (max) 1A resistive load.

The intelligent addressable plant control module should only use one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

The unit should be addressed electronically using a hand-held tool and special lead.

## Intelligent Plant Control Module

The plant control module shall use a single loop address and be loop-powered.  The unit should feature four change-over relay outputs which should be selectable for N/O (normally open) and N/C (normally closed) and four independent inputs for monitoring of volt-free contacts.  Each input should be configurable to monitor either Normally Open or Normally Closed contacts.

The intelligent addressable plant control module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable plant control module should only use one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

The loop powered plant control module should be approved to SIL2.

## Intelligent Conventional Dual Zone Detector Interface Module

The conventional detector interface module shall be capable of monitoring two independent zones, comprising of up to 30 conventional detectors per zone, using a single loop address.

An independent 24 Vdc power supply is required for this module.

The conventional detector interface module shall provide the facility to monitor the detector zones for open or short-circuit and transmit the necessary fault signal to the FACP.

The conventional detector interface module shall provide two remote LEDs to indicate which zones are in alarm and shall provide a red LED to indicate FACP polling.  The unit should also support Schottky Diode head removal.

The conventional detector module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Intelligent Conventional Single Zone Detector Interface Module

The conventional single zone detector interface module shall be capable of monitoring one independent zone of up to 6 conventional detectors using a single loop address.

The conventional single zone detector interface module should be loop-powered.

The conventional single zone detector interface module shall provide the facility to monitor the detector zone for open or short-circuit and transmit the necessary fault signal to the FACP.

The conventional single zone detector interface module shall provide a remote LED facility to indicate when the zone is in alarm and shall provide a red LED to indicate FACP polling.

The conventional single zone detector interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable conventional single zone detector interface module should only have one address and all inputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Intelligent Intrinsically Safe Conventional Detector Interface Module

The Intrinsically safe conventional detector interface module shall be capable of monitoring two independent zones, each of up to 20 intrinsically safe conventional detectors using a single loop address.  This module should be used in conjunction with galvanic isolators or Zener barriers.

An independent 24 Vdc power supply is required for this module.

The Intrinsically safe conventional detector interface module shall provide the facility to monitor the detector zones for open or short-circuit and transmit the necessary fault signal to the FACP.

The Intrinsically safe conventional detector interface module shall provide two remote LEDs to indicate which zones are in alarm and shall provide a red LED to indicate FACP polling.

The intrinsically safe conventional detector interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable intrinsically safe conventional module should only have one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Intelligent Addressable Relay Controller Module

The addressable relay interface module shall be capable of switching two independent relays; either normally open or normally closed, each rated at 30 V, 1 Amp.

A single input shall provide open and short circuit monitoring facilities, set locally at the unit.

The unit shall be powered directly from the addressable loop.

The addressable relay interface module shall provide an LED indication when polled by the FACP.

The addressable relay interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable relay controller module should only have one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

The loop powered addressable relay controller module should be approved to SIL2.

## Intelligent Addressable Mains Relay Controller Module

The addressable mains relay controller module shall be capable of switching one relay; either normally open or normally closed, rated at 250V, 5 Amps.

A single input shall provide open and short circuit monitoring facilities, set locally at the unit.

The addressable mains relay controller module shall use a single loop address.

The unit shall be powered directly from the addressable loop.

The addressable mains relay controller module shall provide an LED indication when polled by the FACP.

The addressable mains relay controller module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable mains relay controller module should only have one address and all inputs/outputs should be sub-addressed to extend the number of addresses.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Intelligent Addressable Input Monitoring Module

The addressable switch monitoring module shall be capable of monitoring two independent voltage free contacts, each normally open or normally closed, using a single loop address.

The unit shall be powered directly from the addressable loop.

The addressable switch-monitoring module shall provide a red LED indication when polled by the FACP.

The LED shall be continuously lit when either input is active.

The addressable switch monitoring module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

The intelligent addressable input monitoring module should only have one address and all inputs/outputs should be sub-addressed to extend the number of addresses. The loop powered sounder base should be approved to SIL2.

Ideally, to save space during installation a DIN rail alternative model should be available.

The addressable input monitoring module should be SIL2.

## Loop Powered Sounder VAD Base

Intelligent addressable electronic sounder VAD bases shall be connected directly to the detection loops.  These shall be able to be mounted onto a standard or short circuit isolator sensor mounting base.  An intelligent addressable smoke sensor, multi-sensor, heat sensor, addressable beacon or an addressable remote indicator may also be mounted onto the sounder VAD base, if required.  The sounder VAD base shall be ceiling or wall mountable.  A cover plate shall be fitted when no other device is to be fitted on the sounder VAD base.

The address of sounders working in conjunction with a sensor base shall be set automatically at the FACP.  The address configured will be above 127 so as not to restrict the number of other addressable devices on the loop.

The loop-powered sounder VAD base volume and tone shall be determined at the FACP.  The loop powered sounder VAD base shall be programmable to have a sound output variable between 50 dB(A) and 98 dB(A) (±2 dB(A)) at 1 metre distance and have a maximum current draw of between 0.8 mA and 21 mA with both sounder and beacon activated simultaneously.  The VAD should employ LED technology to reduce current consumption and maintenance.

The sounder and VAD within the device should have the capability to be operated separately or together, this should be selected at the FACP.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 approved tones.

The sounder VAD base should be approved to EN54-23, Category “O” and be available in either red or white LED versions.

The loop powered sounder base should also be approved to SIL2.

## Loop Powered Sounder Base

Intelligent addressable electronic sounder bases shall be connected directly to the detection loops.  These shall be able to be mounted onto a standard or short circuit isolator sensor mounting base.  An intelligent smoke sensor, multi-sensor, heat sensor, addressable beacon, VAD or an addressable remote indicator may also be mounted onto the sounder base, if required.  The sounder base shall be ceiling or wall mountable.  A cover plate shall be fitted when no other device is to be fitted on the sounder base.

The address of sounders used as sensor bases shall be set automatically at the FACP. The address configured will be above 127 so as not to restrict the number of other addressable devices on the loop.

The loop-powered sounder base volume and tone shall be determined at the FACP. The loop powered sounder base shall be programmable to have a sound output variable between 50 dB(A) and 98 dB(A) (±2 dB(A)) at 1 metre distance and have a maximum current draw of between 0.8 mA and 16 mA.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 approved tones.

The loop powered sounder base should also be approved to SIL2.

## Loop Powered Wall Sounder

The loop powered wall sounder shall be connected directly to the loops where required.  The unit shall be fixed onto a sounder specific mounting base which will be red to match the sounder.  A weatherproof kit should be available to increase the IP Rating of the wall sounder to IP66.

The Wall Sounder sound output should be variable between 90 dB(A) and 102 dB(A) (±2 dB(A)) and should have a maximum current draw of between 2 mA and 8 mA depending on the tone used.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 approved tones.

The loop powered wall sounder should also be approved to SIL2.

## Loop Powered Wall Sounder VAD (Wall Sounder Beacon)

The loop powered wall sounder VAD shall be connected directly to the loops where required.  The unit shall be fixed onto a sounder specific mounting base which will be red to match the sounder.  A weatherproof kit should be available to increase the IP Rating of the wall sounder to IP66.

The VAD lens should be transparent and utilise LED technology to reduce current consumption and maintenance.

The wall sounder VAD sound output should be variable between 90 dB(A) and 102 dB(A) (±2 dB(A)) and should have a maximum current draw of between 2 mA and 13 mA depending on the tone used and with both sounder and beacon activated simultaneously.

The sounder and VAD within the device should have the capability to be operated separately or together, this should be selected at the FACP.

The unit should be capable of producing all 51 (fifty-one) EN54 approved tones.

The wall sounder VAD base should be approved to EN54-23, Category “O” and be available in either red or white LED versions.

The wall sounder VAD should be approved to SIL2

## Loop Powered Wall VAD (Wall Beacon)

The loop-powered wall VAD should contain a free-form optic designed to produce a highly visible flash which should meet the cubic light volume coverage requirements of EN54-23.  The flash frequency should be 0.5/1 Hz at an operating voltage of 17-41 V dc. The unit should fit directly onto the standard sensor mounting base.

The loop powered wall VAD base should be approved to EN54-23, Category “W” and be available in either red or white LED versions.  Coverage volume based on a 2.4m ceiling height should be a cube measuring 5m, 6m or 7m on the sides, programmable from the FACP.

## Loop Powered Ceiling VAD (Ceiling Beacon)

The loop-powered ceiling VAD should contain a free-form optic designed to produce a highly visible flash which should meet the cylindrical light volume coverage requirements of EN54-23.  The flash frequency should be 0.5/1 Hz at an operating voltage of 17-41 V dc. The unit should fit directly onto the standard sensor mounting base.

The loop powered ceiling VAD base should be approved to EN54-23, Category “C” and be available in either red or white LED versions.  Coverage volume based on a 3m ceiling height should be a cylinder measuring a diameter of 1.5m, 6.5m, 7.9m, 8.6m, 10m, 11.4m or 15.1m, programmable from the FACP.

## Hand Held Address Programmer

This unit should be capable of electronically addressing analogue devices such as sensors, beacons, VADs, remote indicators, sounder bases, sounder/beacon bases and (with an optional lead) manual call points.  It should also be capable of listing six different fault codes relating to the device that is being programmed.  This programmer should also be capable of reading the device’s current analogue value.

## Conventional Optical Smoke Detectors

The optical smoke detectors shall be capable of detecting visible combustion gases emanating from fires and shall employ the forward light-scatter principle.

The optical smoke chamber shall be equally sensitive to a wide range of combustible materials and incorporate flat response technology.  The operating voltage range of the Conventional Detector shall be 9.5 Vdc to 30 Vdc.  The Detector should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the detector, once locked onto the base the detector can only be removed with a special removal tool.

The design of the point-type optical smoke detector sensing chamber shall be optimised to minimise the effect of dust deposit over a period of time.  The chamber cover shall be removable for ease of cleaning or replacement.

The point-type optical smoke detectors shall incorporate screens designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).

The optical smoke detectors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

The manufacturer shall have available the following versions of the point type optical smoke detector to meet different applications:

Conventional

Conventional – Intrinsically Safe

Marine Approved

SIL2 compliant

The optical smoke detector shall incorporate two LEDs, clearly visible from the outside, to provide indication of alarm actuation.

In locations where the detector is not readily visible, remote indicator units shall be provided.

## Conventional Heat Detectors

The heat detectors shall be capable of detecting rapid rise in temperature and/or fixed absolute temperatures.

The heat detectors shall employ two heat-sensing elements with different thermal characteristics to provide a rate of rise dependent response.

The heat detectors shall include RFI screening to minimise the effect of radiated and conducted electrical interference.  The Detector should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the detector, once locked onto the base the detector can only be removed with a special removal tool.

The manufacturer shall have available the following versions of heat detectors to meet different applications:

Conventional Fixed Temp./Rate of Rise – Class A and Class C

Conventional – Intrinsically Safe – Grade 1

Conventional – IP67 rated at 60 degrees

The heat detectors shall incorporate two LEDs, clearly visible from the outside, to provide an indication of alarm actuation.

In locations where the detector is not readily visible, remote indicator units shall be provided.

## Conventional Optical Beam Smoke Detectors

The optical beam smoke detectors shall be capable of detecting visible combustion gases emanating from fires and shall utilise the light obscuration principle. The emitter shall project a near infra-red beam to the receiver.

The optical beam smoke detectors shall consist of an emitter and a receiver pair. The detectors shall operate over a 5 – 100 metre range providing a maximum coverage of 1500 m².

The optical beam smoke detectors shall have automatic recalibration in order to adjust for contamination.

The optical beam smoke detectors shall be designed to have high resistance to corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

The optical beam smoke detectors shall incorporate two LEDs, clearly visible from the outside and below, to provide indication of alarm actuation and fault.

## Conventional Single Infra-Red Flame Detectors

The single flame detector shall be of a point-type.  It shall be mounted on its base using a simple twist action for ease of installation and removal.  The flame detector should feature twin fire LEDs.

The class 1 flame detector shall be able to detect infra-red emissions in a 120( cone of vision, in a direct line of sight up to 25m.

## Conventional Triple Infra-Red Flame Detectors

The triple flame detector shall incorporate solar blind technology detecting 0.1m at 25m and responds to low frequency IR radiation between 1 to 15Hz.

The class 1 flame detector should have selectable output options, conventional 2-wire, 4-20mA latching or non-latching relay contacts, fire, fault and pre-alarm.

## Conventional Electronic Sounders

Electronic sounders shall be acceptable and powered by 24 Vdc from the FACP or a sounder control module.

Non-loop-powered versions shall be flush or surface mountable, red in colour.  They shall have a minimum sound output of 110 dB(A) at 1 metre distance and shall have a maximum current consumption at 24 Vdc of 100 mA.

32 user selectable tones should be available and an IP66 variant should be available.

## Air Sampling Smoke Detection System

The air sampling smoke detection system shall comprise detector units/panels featuring an internal fan which are connected to a sampling pipe (or a series of sampling pipes).  The detector unit shall continually sample the air in a particular area and by use of laser particle detection technology shall recognise the presence of airborne pollutants (smoke) at very low levels (High Sensitivity Smoke Detection).

The detector units should be capable of interacting with the analogue fire system loop by way of a suitable internally mounted control module.  The units shall also feature fire and fault relays for remote monitoring by the local fire detection system or a BMS system.

An RS485 communications bus should be provided as standard for networking several units together and for remote communications.

Several detection units shall be able to be controlled from one “command” unit.  This command unit shall be able to display information and control remotely the “slave” detection units.

## Alarm Bells

Fire alarm bells shall be under-dome type with a high resonance pressed alloy-steel gong to ensure a loud clear-tone ring. They shall be fully suppressed and polarised.

The operating mechanism shall be fully enclosed, and the gong shall be red stove enamelled for long life.

## Duct Probe Housing

The manufacturer shall produce standard equipment for the installation of smoke detectors in air ducts.  This equipment shall be designed to accommodate the manufacturer’s intelligent addressable smoke sensors and conventional.

The duct probe housing should utilise one probe per housing and can be mounted on a round or square duct with an additional bracket.

A test hole on the cover shall be provided for ease of testing and an air flow indicator should be visible through the cover to provide indication that there is sufficient air flow through the housing.

# System Delivery

The specialist fire system contractor must be able to demonstrate competence by means of a valid manufacturer endorsed certificate relating to the products associated with this project.

The specialist fire system contractor must also be able to demonstrate competence by means of valid certification for technical accreditation by one of the following assessment bodies:

LPS1014

BAFE SP203

ECA / FSA Category A3

The accreditation must be specifically relevant to the specialist fire system contractor being positioned to certify their work in the following modules:

Design

Installation

Commissioning

Maintenance

Verification

END OF SPECIFICATION

Hochiki Europe (UK) Ltd. reserves the right to alter the specification of its products from time to time without notice. Although every effort has been made to ensure the accuracy of the information contained within this document it is not warranted or represented by Hochiki Europe (UK) Ltd. to be a complete and up-to-date description.  Please check our web site for the latest version of this document.