# Standards

The system shall be fully compliant with the following standards:

BS 5839-1:2013

EN 54 Parts 3, 5,7,11, 17, 18, 23 & 25

EN 300-220 Part 1

# Function

The system shall be capable of providing a wireless analogue addressable fire solution.

The system shall have the capability to allow wired field devices to be combined on the same loop wiring as the wireless translator modules to form a seamless hybrid system.

# System Capacity and General Operation

The system shall have a range of battery powered fully intelligent, analogue field devices, comprising of at least:

Optical Smoke Sensor

Thermal Heat Sensor (Rate of Rise and Fixed Temperature with a classification of A1R)

Combined Optical/Thermal Multi Criteria Sensor (selectable modes)

Call Point

Wall Mounted Sounder

Optical Smoke Sensor with Voice Alarm and integral VAD

Monitored Input Module

Output Module

All wireless sensors shall have automatic drift compensation for the effects of dirt and temperature.

# Translators Modules

The system shall utilise loop Translator modules to integrate the wireless and wired elements of the system and these should be approved to EN54-17, 18 and 25

Each Translator shall be capable of communicating with a maximum of 126 field devices, this includes Expanders, in other words the 126 capacity can be a combination of both field devices and Expanders, or all field devices.

Translator modules shall take their power from the communication loop and should not require a separate Power Supply Unit.

Translator units should be fully monitored by the Fire Alarm control equipment.

Translators should be programmable without the need of special tools or software.

A PC link should be available for the Translator, to make the programming of larger systems easier.

Translator and Expander Modules shall be self-optimising in regard to wireless amplitude and frequency.

The Translator module should incorporate an integral short-circuit isolator.

The Translator should be RED (Radio Equipment Directive) compliant, to EN 300-220 Part 1.

.

# Expander Modules

The system shall have the facility to use Expander Modules to boost the signal strength and coverage of the Translator Modules where required.

Where Expander Modules require a separate PSU this should be monitored.

The Expander should be capable of working on voltages between 10 – 27 VDC.

When using two or more Expanders, these should form a self-configuring mesh network allowing any field device to connect and communicate to the Translator through any available Expander.

The Expander should be RED (Radio Equipment Directive) compliant, to EN 300-220 Part 1.

# Power Supply & Batteries

All system field device components shall be powered by standard off-the-shelf Lithium batteries. No special battery packs or non-standard cells will be used.

All field devices will have two independent lithium battery supplies. A primary cell to power the device under normal conditions and a secondary cell to maintain the operation of the device should the primary fail.

The field device primary battery life should provide up to a maximum of 10 years, dependent on operational usage:

Detectors, Call Points and Input Modules

Primary Cell – up to 10 Years

Secondary Cell - 3 Months

Warning and Output Devices

Primary Cell – up to 10 Years

Secondary Cell – 8 Months

# Field Programming

The system shall be programmable, configurable and expandable in the field without the need for special tools or electronic equipment and shall not require field replacement of electronic integrated circuits.

All programming shall be accomplished through the on-board programming buttons (in the case of Translators) or via a P.C. based configuration package.

All field-defined programs shall be stored in non-volatile memory.

# Radio Communications

The system should incorporate a Bi-Directional radio protocol where the field devices can communicate with the Translator and the Translator with the devices.

The system shall utilise the licence free 868MHz range and communicate across 6 discrete channels. Each field device will have the capability to independently hop between these channels to establish the best communication path with the Translator.

The communication, in open air, between system components shall equal or surpass the following:

| Between Translators and Expanders | 2000 metres |
| --- | --- |
| Between Expanders and Field Devices | 1200 metres |

Expanders will form a mesh network that will be self-configuring, i.e. devices not tied to specific Expanders, to ensure an ‘always on’ connection back to the Translator.  Field devices will have the ability to choose and connect to the strongest Expander signal in the event of signal disruption.

All field devices will utilise automatic and independent amplitude control and will optimise their wireless output to suit the device location and site conditions.

Each system will have a unique site code ensuring that interference with or from adjacent system does not take place.

# Test & Diagnostic Equipment

The system will have PC based programming, diagnostic and commissioning software for use when designing, commissioning or testing the system.

The system shall include a portable site survey tool which will determine signal strength of field devices in their prospective locations prior to installation.

This kit will comprise of:

RF Signal Scanner

Test Sensor Head

END OF SPECIFICATION

Hochiki Europe (UK) Ltd. reserves the right to alter the specification of its products from time to time without notice. Although every effort has been made to ensure the accuracy of the information contained within this document it is not warranted or represented by Hochiki Europe (UK) Ltd. to be a complete and up-to-date description.  Please check our web site for the latest version of this document.